Section 08 81 00 according to CSI MasterFormat 2004

Fired-Rated Glass: SCHOTT PYRAN® Platinum F glass-ceramic

Part 1 – General

1.1 Summary

A. Section Includes:

1. Fire-rated glazing materials intended for use in door lights, transoms, windows and sidelites in fire-rated frames.

B. Related Sections:

1. Section 08 11 00 – Metal Doors and Frames
2. Section 08 12 00 – Metal Frames
3. Section 08 13 00 – Metal Doors
4. Section 08 14 00 – Wood Doors
5. Section 08 51 00 – Metal Windows
6. Section 08 52 00 – Wood Windows

1.2 References

1. UL 9 – Fire Tests of Window Assemblies
2. UL 10B – Fire Tests of Door Assemblies
3. UL 10C – Positive Pressure Fire Tests of Door Assemblies
4. UBC 7-2 – Positive Pressure Standard
5. UBC 7-4 – Fire Test of Window Assemblies
6. NFPA 80 – Fire Doors and Windows
7. NFPA 252 – Fire Tests of Door Assemblies
8. NFPA 257 – Fire Tests of Window Assemblies
9. ULC CAN4-S104 – Fire Tests of Door Assemblies
10. ULC CAN4-S106 – Fire Tests of Window Assemblies

1.3 Performance Requirements

1. Fire- and safety-rated glass-ceramic, clear and wireless with a surface-applied film, for use in door lights, transoms or sidelights and windows with fire rating requirements from 20 minutes to 90 minutes (180 minutes in doors) with hose stream test in impact safety-rated locations.
2. Conforms to positive pressure test standards.
3. Environmentally-friendly glass-ceramic product and manufacturing process
	1. Conservation of energy and water in manufacturing process: 20% electricity from renewable sources, gray water replaces 90 % of process water, all process water recirculated
	2. Raw material batch includes 40 – 50 % recycled cullet sourced internally and from cut-offs and scrap returned from fabricators
	3. Environmentally friendly glass-ceramic contains no hazardous heavy metals such as Antimony or Arsenic.

1.4 Submittals

A. Comply with requirements of Section 01 30 00.

B. Product data: Submit manufacturer’s technical data for each glazing material required, including installation and maintenance instructions.

1. Certificate of Compliance from glazing material fabricator attesting that glazing materials furnished for project comply with CPSC requirements. Glazing materials bear manufacturers permanent label designating type of glass, fire rating and UL Mark. Provided labels represent a quality control program involving a recognized certification agency or independent testing laboratory acceptable to authority having jurisdiction.
2. Product test listings: From UL indicating fire-rated glass complies with requirements, based on comprehensive testing of current product.

C. Samples: Submit, for verification and approval purposes.

1.5 Quality Assurance

A. Glazing standards: GANA Glazing Manual and GANA Sealant Manual

B. Fire-rated glass: Each lite shall bear a permanent, non-removable label from Underwriters Laboratories certifying it for use in tested and rated fire-protective assemblies.

1.6 Delivery, Storage and Handling

A. Deliver, store and handle materials under provision of Section 01 60 00.

B. Deliver materials to specified destination in manufacturers or distributors packaging, undamaged, complete with installation instructions.

C. Store off ground, under cover, protected from weather and construction activities.

1.7 Warranty

Provide manufacturers limited warranty under provision of Section 01 70 00.

Part 2 – Products

2.1 Fire-Rated Glazing Materials

A. Manufacturer: PYRAN® Platinum F fire- and safety rated glass-ceramic manufactured by SCHOTT Technical Glass Solutions GmbH, Jena, Germany and supplied by SCHOTT North America, Inc., Louisville, KY, Telephone 1.502.657.4439, Fax 1.502.966.4976.

B. Properties:

* 1. Thickness: 3/16” (5 mm)
	2. Film: surface-applied safety film
	3. Weight: 2.5 lbs/ft².
	4. Clear; No amber tint
	5. Visible light transmission: approximately 80 % according to test standard DIN EN 410
	6. Fire-rating: Up to 90 minutes (up to 180 minutes in doors) with hose stream test
	7. Impact safety rating: ANSI Z97.1 (Class A) and CPSC 16CFR1201 (Cat. I and II).
	8. Manufactured by a special float process resulting in smooth surface finish
	9. Environmentally friendly glass-ceramic contains no hazardous heavy metals such as Antimony or Arsenic.

C. Maximum sheet sizes: Approximately 51” x 99”

D. Labelling: Permanently label each lite of PYRAN® Platinum F fire- and safety-rated glass-ceramic with product and manufacturers name, UL-mark, fire rating, etc., according to code requirements.

1. Optional: Glazing may be lightly sandblasted or may be decorated with surface-applied opacity film. After the surface treatment, a Clearshield coating may be applied.
2. The glazing units may be directly screen-printed upon.

E. Fire Rating: Fire rating tested and listed by UL for fire rating scheduled at opening locations on drawings, when tested in accordance with UL 9, UL 10C, UBC 7-2, UBC 7-4, NFPA 252, NFPA 257, ULC CAN4-S106 and ULC CAN4-S106.

2.2 Glazing Compound

A. Glazing tape: Closed cell polyvinyl chloride (PVC) foam, Pemko Manufacturing Company, Ref. FG3000S90 or Unifrax Corporation Fiberfrax Alumino-Silicate fiber glazing tape.

B. Setting blocks: Calcium silicate

C. Cleaners, primers and sealers: Type recommended by manufacturer of glass and gaskets.

2.3 Fabrication

A. Fabricate glass and other glazing products in sizes required to glaze openings indicated for project, with edge and face clearances, edge and surface conditions, and bite complying with recommendations of product manufacturer and referenced glazing standard as required to comply with system performance requirements.

Part 3 – Execution

3.1 Examination

A. Examine glass and framing, with glaziers present, for compliance with the following:

1. Manufacturing and installation tolerances, including those for size, squareness, offsets at corners.
2. Minimum required face or edge clearances.
3. Observable edge damage or surface imperfections.

B. Do not proceed with glazing until unsatisfactory conditions have been corrected.

C. Clean glazing channels and other framing members receiving glass immediately before glazing. Remove coatings that are not firmly bonded to substrates.

3.2 Installation (glazing)

A. Comply with referenced GANA manuals and instructions of manufacturers of glass, glazing sealants and glazing compounds.

B. Protect glass from edge damage during handling and installation. Inspect glass during installation and set aside pieces with edge damage that could affect the performance.

C. Set units of glass in each series with uniformity of pattern, draw, bow and similar characteristics.

D. Cut glazing tape to length and set against permanent stops, flush with sight lines to fit openings exactly, with stretch allowance during installation.

E. Arrange two setting blocks located at quarter points of glass with edge block no more than six inches from corners.

F. Glaze vertically into labelled fire-rated metal frames or partition walls with the same fire rating as the glass and push against tape for full contact at perimeter of pane or unit.

G. Place glazing tape on free perimeter of glazing in same manner described above.

H. Install removable stop and secure without displacing the tape.

I. Install so that appropriate markings remain permanently visible.

3.3 Protection and cleaning

A. Protect glass from contact with contaminating substances resulting from construction operations. Remove any such substances by methods approved by the glass manufacturer.

B. Wash glass on both surfaces not more than four days prior to date scheduled for inspections intended to establish date of substantial completion. Wash glass with a soft, clean, non-abrasive cloth and a mild soap, detergent, or non-abrasive window cleaning solution. After cleaning, rinse immediately with clean water and remove any excess water from the panel surface. Do not allow any metal parts of the cleaning equipment to come in contact with the panel surface.

3.4 Glazing schedule Rating

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Rating | Application  | Max. exposed area of glazing in. (m²)  | Max. width of exposed glazing in. (mm)  | Max. height of exposed glazing in. (mm)  | Min. depth of groovein. (mm)  | Groove Width In.  | Building Code Marking  |
| Up to 90 min  | Doors Non-Temp Rise  | 3708 (2.39 m2)  | 36” (914 mm)  | 76” (1930 mm)  | 5/8” (16 mm)  | 7/16” 3/8”  | D-H-NT-90  |
| Up to 180 min  | Doors Temp Rise and Non-Temp Rise  | 100” (0.0645 m²)  | 12” (305 mm)  | 33” (838 mm)  | ½” (12.7 mm)  | 7/16” 3/8”  | D-H-NT-180  |
| Up to 90 min  | Transom lites, sidelites, windows  | 4933” (3.183 m²)  | 98 ¼”(2495 mm)  | 98 ¼” (2495 mm)  | 5/8” (16 mm)  | 7/16” 3/8”  | OH-90  |

End of Section